# Thermal Imaging Report

# 1. Overview

Date: October 24, 2026
Equipment: FLIR T865
Technician: Jane Smith

# 2. Thermal Findings

## Roof Level (Southwest Corner)

Finding: Significant thermal anomaly detected around the primary drain area. Severe temperature drop of 4.2°C compared to surrounding membrane, strongly indicating subsurface moisture saturation (water trapped under the membrane).

## Server Room

Finding: The secondary cooling unit is showing a hotspot of 65°C on the compressor casing, which is 20°C above expected operating parameters. Suggests imminent overheating or mechanical friction issue.

## North Wall Foundation

Finding: Slight thermal bridging noted along the baseline. No major insulation gaps detected, but cooling pattern matches the structural cracking seen visually.